ANNUAL FIRE SAFETY REPORT

Year: 2026

Note: Fire Safety Managers (FSMs) and Building Owners are advised to periodically update and review the Annual Fire Safety Report. This report should include up-to-date information on fire safety within the premises and rectification measures taken to ensure a fire-safe environment.

BUILDING INFORMATION

| Name of Building | Pioneer Tech Hub |
| --- | --- |
| Address | 15 Jurong West Ave 5, Singapore 648216 |
| No. of Storeys | 5 |
| Gross Floor Area (GFA) | 6200 m² |
| Occupant Load (OL) | 210 |

PROVISION OF EMERGENCY PREPAREDNESS (EP) MEASURES

| S/No | EP Measure | Details |
| --- | --- | --- |
| 1 | Emergency Response Plan (ERP) | Updated annually — refer to Building Management |
| 2 | Validity of Fire Certificate (FC) | Please verify with SCDF records |
| 3 | Name of Appointed FSM | John Tan |
| 4 | CERT Members | As per building emergency team register |

RECORD OF TRAINING CONDUCTED

| Category | Date | Description | No. of Participants |
| --- | --- | --- | --- |
| Occupants / Tenants | 2026 | Annual Fire Safety Briefing | - |
| Company Emergency Response Team (CERT) | 2026 | CERT Training / Table-Top Exercise | - |
| Fire Wardens | 2026 | Fire Warden Briefing | - |

FIRE EVACUATION DRILLS CONDUCTED

| S/N | Building | Date | Participants | Time Taken | Issues Faced | Result |
| --- | --- | --- | --- | --- | --- | --- |
| 01 | Pioneer Tech Hub | 2026-07-24 | 2 | - | w | Completed |
| 02 | Pioneer Tech Hub | 2026-07-21 | 5 | - | N/A | Completed |
| 03 | Pioneer Tech Hub | 2026-06-09 | 210 | - | Good | Completed |
| 04 | Pioneer Tech Hub | 2026-07-21 | 200 | 0315 | Test | Completed |
| 05 | Pioneer Tech Hub | 2026-06-05 | 210 | - | N/A | Completed |
| 06 | Pioneer Tech Hub | 2026-07-21 | 2 | - | 2 | Completed |
| 07 | Pioneer Tech Hub | 2026-07-15 | 2 | - | T | Completed |
| 08 | Pioneer Tech Hub | 2026-07-17 | 2 | - | 2 | Completed |
| 09 | Pioneer Tech Hub | 2026-06-25 | 210 | - | qqe | Completed |
| 10 | Pioneer Tech Hub | 2026-01-12 | 36 | 00:04:20 | No critical issue found. | Passed |
| 11 | Pioneer Tech Hub | 2026-01-26 | 40 | 00:05:20 | No critical issue found. | Passed |
| 12 | Pioneer Tech Hub | 2026-02-09 | 44 | 00:06:20 | No critical issue found. | Passed |
| 13 | Pioneer Tech Hub | 2026-02-23 | 48 | 00:04:20 | Assembly-area sign was difficult to see. | Completed with Follow-Up |
| 14 | Pioneer Tech Hub | 2026-03-09 | 52 | 00:05:20 | No critical issue found. | Passed |
| 15 | Pioneer Tech Hub | 2026-03-23 | 56 | 00:06:20 | No critical issue found. | Passed |
| 16 | Pioneer Tech Hub | 2026-04-13 | 60 | 00:04:20 | No critical issue found. | Passed |
| 17 | Pioneer Tech Hub | 2026-04-27 | 64 | 00:05:20 | No critical issue found. | Passed |
| 18 | Pioneer Tech Hub | 2026-05-18 | 68 | 00:06:20 | No critical issue found. | Passed |

REVIEW OF FIRE EVACUATION DRILLS

| S/N | Issues Faced | Recommendations |
| --- | --- | --- |
| 1 | w | w |
| 2 | Good | good |
| 3 | Test | Tje |
| 4 | 2 | 2 |
| 5 | T | Y |
| 6 | 2 | 2 |
| 7 | qqe | q23 |
| 8 | Wardens swept assigned zones and occupants proceeded calmly to the assembly area. | Continue regular warden briefings. |
| 9 | Wardens swept assigned zones and occupants proceeded calmly to the assembly area. | Continue regular warden briefings. |
| 10 | Wardens swept assigned zones and occupants proceeded calmly to the assembly area. | Continue regular warden briefings. |
| 11 | Wardens swept assigned zones and occupants proceeded calmly to the assembly area. | Continue regular warden briefings. |
| 12 | Wardens swept assigned zones and occupants proceeded calmly to the assembly area. | Continue regular warden briefings. |
| 13 | Wardens swept assigned zones and occupants proceeded calmly to the assembly area. | Continue regular warden briefings. |
| 14 | Wardens swept assigned zones and occupants proceeded calmly to the assembly area. | Continue regular warden briefings. |
| 15 | Wardens swept assigned zones and occupants proceeded calmly to the assembly area. | Continue regular warden briefings. |
| 16 | Wardens swept assigned zones and occupants proceeded calmly to the assembly area. | Continue regular warden briefings. |

FINDINGS OF FIRE SAFETY CHECKS & RECTIFICATION WORKS

| S/N | Date | Building | Issue Identified | Rectification Taken |
| --- | --- | --- | --- | --- |
| 1 | 13/06/2026 | Pioneer Tech Hub | Main Fire Alarm Panel | Inspect and repair faulty component. |
| 2 | 25/06/2026 | Pioneer Tech Hub | Main Supply Indicator | Pending rectification |
| 3 | 01/07/2026 | Pioneer Tech Hub | Obstruction | Remove obstruction and maintain clear access. |
| 4 | 17/07/2026 | Pioneer Tech Hub | Means of Escape | test124 |
| 5 | 01/07/2026 | Pioneer Tech Hub | Obstruction along escape staircases / door | Relocate the bicycle, check and re-tag the hose reel, and reinstate or replace the loose cover. |
| 6 | 01/07/2026 | Pioneer Tech Hub | Fireman switch | Label message buttons, place a hard copy message script at the PA panel, and conduct a PA system and speaker audit. |
| 7 | 15/07/2026 | Pioneer Tech Hub | Fire Extinguishers | test124 |
| 8 | 01/07/2026 | Pioneer Tech Hub | Main Fire Alarm Panel | Engage a qualified fire alarm contractor to diagnose the fault, inspect the panel’s power supply, batteries, wiring, detection loops, and communication modules, and repair or replace defective components. Perform a complete functional test after rectification and document the results. Implement temporary monitoring measures until the system is restored. |
| 9 | 22/07/2026 | Pioneer Tech Hub | Main Supply Indicator | Engage a qualified fire alarm contractor to diagnose the fault, inspect the panel’s power supply, batteries, wiring, detection loops, and communication modules, and repair or replace defective components. Perform a complete functional test after rectification and document the results. Implement temporary monitoring measures until the system is restored. |
| 10 | 24/07/2026 | Pioneer Tech Hub | Zone Indicators | test |
| 11 | 24/07/2026 | Pioneer Tech Hub | Standby Battery / Charger | Re paint it |
| 12 | 24/07/2026 | Pioneer Tech Hub | Fire Hosereel serviceable? | Engage a qualified fire alarm contractor to diagnose the fault, inspect the panel’s power supply, batteries, wiring, detection loops, and communication modules, and repair or replace defective components. Perform a complete functional test after rectification and document the results. Implement temporary monitoring measures until the system is restored. |
| 13 | 21/07/2026 | Pioneer Tech Hub | Signboard / label | Pending rectification |
| 14 | 22/07/2026 | Pioneer Tech Hub | Exit doors unlocked | Pending rectification |
| 15 | 01/07/2026 | Pioneer Tech Hub | Valve at open position strapped & locked | Replace straps and locks with proper labelling. |
| 16 | 01/07/2026 | Pioneer Tech Hub | Signboard / label | Reinstate the missing labelling. |
| 17 | 10/06/2026 | Pioneer Tech Hub | Obstruction | Remove obstruction and maintain clear access. |
| 18 | 10/06/2026 | Pioneer Tech Hub | Obstruction along escape staircases / door | Relocate the bicycle, check and re-tag the hose reel, and reinstate or replace the loose cover. |
| 19 | 10/06/2026 | Pioneer Tech Hub | Fireman switch | Label message buttons, place a hard copy message script at the PA panel, and conduct a PA system and speaker audit. |
| 20 | 10/06/2026 | Pioneer Tech Hub | Valve at open position strapped & locked | Replace straps and locks with proper labelling. |
| 21 | 10/06/2026 | Pioneer Tech Hub | Signboard / label | Reinstate the missing labelling. |
| 22 | 26/06/2026 | Pioneer Tech Hub | Main Fire Alarm Panel | Faulty |
| 23 | 24/07/2026 | Pioneer Tech Hub | Pressure fan at staircases | X |
| 24 | 24/07/2026 | Pioneer Tech Hub | Main Fire Alarm Panel | Faulty |
| 25 | 28/06/2026 | Pioneer Tech Hub | Obstruction along escape staircases / door | Relocate the bicycle, check and re-tag the hose reel, and reinstate or replace the loose cover. |
| 26 | 05/06/2026 | Pioneer Tech Hub | Test1 | Test1 |
| 27 | 12/01/2026 | Pioneer Tech Hub | Zone indicator lamp dim | Replace the indicator lamp and function-test the panel. |
| 28 | 26/01/2026 | Pioneer Tech Hub | Hose reel access obstructed | Remove cartons and mark the keep-clear area. |
| 29 | 09/02/2026 | Pioneer Tech Hub | Extinguisher partially obstructed | Relocate the display and restore clear access. |
| 30 | 23/02/2026 | Pioneer Tech Hub | Escape route obstruction | Remove stored items and brief the tenant. |
| 31 | 09/03/2026 | Pioneer Tech Hub | Exit light not illuminated | Replace the battery pack and retest the fitting. |
| 32 | 23/03/2026 | Pioneer Tech Hub | Sprinkler valve strap worn | Install a new labelled strap and lock. |
| 33 | 13/04/2026 | Pioneer Tech Hub | Control valve label faded | Install a new permanent identification label. |
| 34 | 27/04/2026 | Pioneer Tech Hub | Dry riser inlet paint faded | Clean and repaint the breeching inlet. |
| 35 | 18/05/2026 | Pioneer Tech Hub | Access route encroachment | Remove the items and reinforce the no-storage rule. |

SCHEDULE OF FIRE SAFETY ACTIVITIES FOR 2027

| S/N | From | To | Brief Description of Activity |
| --- | --- | --- | --- |
| 1 | Jan 2027 | Dec 2027 | Monthly on-site fire safety inspections |
| 2 | Apr 2027 | Apr 2027 | Fire Warden Briefing / Table-Top Exercise |
| 3 | May 2027 | May 2027 | Fire Evacuation Drill (1st) |
| 4 | Aug 2027 | Aug 2027 | Fire Safety Equipment Servicing Review |
| 5 | Sep 2027 | Sep 2027 | Basic Fire Fighting Hands-on Training |
| 6 | Nov 2027 | Nov 2027 | Fire Evacuation Drill (2nd) |

MATTERS ARISING FROM PREVIOUS REPORT

| S/N | Issue(s) | Action(s) Taken |
| --- | --- | --- |
| 1 | Main Supply Indicator | Pending rectification — follow-up in progress |
| 2 | Obstruction | Remove obstruction and maintain clear access. |
| 3 | Obstruction along escape staircases / door | Relocate the bicycle, check and re-tag the hose reel, and reinstate or replace the loose cover. |
| 4 | Fireman switch | Label message buttons, place a hard copy message script at the PA panel, and conduct a PA system and speaker audit. |
| 5 | Main Fire Alarm Panel | Engage a qualified fire alarm contractor to diagnose the fault, inspect the panel’s power supply, batteries, wiring, detection loops, and communication modules, and repair or replace defective components. Perform a complete functional test after rectification and document the results. Implement temporary monitoring measures until the system is restored. |
| 6 | Zone Indicators | test |
| 7 | Standby Battery / Charger | Re paint it |
| 8 | Signboard / label | Pending rectification — follow-up in progress |
| 9 | Exit doors unlocked | Pending rectification — follow-up in progress |
| 10 | Valve at open position strapped & locked | Replace straps and locks with proper labelling. |
| 11 | Signboard / label | Reinstate the missing labelling. |
| 12 | Obstruction along escape staircases / door | Relocate the bicycle, check and re-tag the hose reel, and reinstate or replace the loose cover. |
| 13 | Fireman switch | Label message buttons, place a hard copy message script at the PA panel, and conduct a PA system and speaker audit. |
| 14 | Valve at open position strapped & locked | Replace straps and locks with proper labelling. |
| 15 | Signboard / label | Reinstate the missing labelling. |
| 16 | Pressure fan at staircases | X |
| 17 | Dry riser inlet paint faded | Clean and repaint the breeching inlet. |
| 18 | Access route encroachment | Remove the items and reinforce the no-storage rule. |

ARSON PREVENTION PLAN (APP)

A) Identifying Critical Locations of Fire Safety Systems

• Ensure the Genset room, Switch Room, and Lift Motor Room are always neat and tidy.

• Ensure there is no leakage in the petroleum storage area.

• All fire protection equipment rooms are to remain locked and accessible only to authorised personnel.

B) Identifying Fire Hazards

• Regular checks to be conducted to ensure no accumulation of combustible materials in common areas.

• All discarded items and rubbish to be disposed of promptly.

• Storage areas to be inspected monthly for fire hazard compliance.

C) Preventive Measures

• CCTV surveillance maintained at all entry/exit points and fire risk areas.

• All abnormalities to be reported to the FSM immediately.

• Building Management to ensure contractor activities are supervised at all times.

CERTIFICATION

I hereby certify that this Annual Fire Safety Report has been prepared accurately and reflects the fire safety activities conducted during the year in accordance with the requirements of the Fire Safety Act (Cap. 109A).

Name of Fire Safety Manager:  John Tan

Signature:  _______________________________

Date:  24 Jul 2026

— End of Annual Fire Safety Report —